## Complete Map
Fronius Datamanager Register Map: Integer Meter Model (201, 202, 203)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device model | String32
40037 | 40044 | 8 | R | 0x03 | Opt | Options | String16
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of meter | String16
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the meter | String32
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1-247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Meter Modbus Map; 201: single phase, 202: split phase, 203: three phase | uint16 |  |  | 201, 202, 203
40071 | 40071 | 1 | R | 0x03 | L | Length of inverter model block | uint16 | Registers |  | 105
40072 | 40072 | 1 | R | 0x03 | A | AC Total Current value | int16 | A | A_SF
40073 | 40073 | 1 | R | 0x03 | AphA | AC Phase-A Current value | int16 | A | A_SF
40074 | 40074 | 1 | R | 0x03 | AphB | AC Phase-B Current value | int16 | A | A_SF
40075 | 40075 | 1 | R | 0x03 | AphC | AC Phase-C Current value | int16 | A | A_SF
40076 | 40076 | 1 | R | 0x03 | A_SF |  | sunssf | sunssf
40077 | 40077 | 1 | R | 0x03 | PhV | AC Voltage Average Phase-to-neutral value | int16 | V | V_SF
40078 | 40078 | 1 | R | 0x03 | PhVphA | AC Voltage Phase-A-to-neutral value | int16 | V | V_SF
40079 | 40079 | 1 | R | 0x03 | PhVphB | AC Voltage Phase-B-to-neutral value | int16 | V | V_SF
40080 | 40080 | 1 | R | 0x03 | PhVphC | AC Voltage Phase-C-to-neutral value | int16 | V | V_SF
40081 | 40081 | 1 | R | 0x03 | PPV | AC Voltage Average Phase-to-phase value | int16 | V | V_SF
40082 | 40082 | 1 | R | 0x03 | PPVphAB | AC Voltage Phase-AB value | int16 | V | V_SF
40083 | 40083 | 1 | R | 0x03 | PPVphBC | AC Voltage Phase-BC value | int16 | V | V_SF
40084 | 40084 | 1 | R | 0x03 | PPVphCA | AC Voltage Phase-CA value | int16 | V | V_SF
40085 | 40085 | 1 | R | 0x03 | V_SF |  | sunssf | sunssf
40086 | 40086 | 1 | R | 0x03 | Hz | AC Frequency value | int16 | Hz | Hz_SF
40087 | 40087 | 1 | R | 0x03 | Hz_SF |  | sunssf | sunssf
40088 | 40088 | 1 | R | 0x03 | W | AC Power value | int16 | W | W_SF
40089 | 40089 | 1 | R | 0x03 | WphA | AC Power Phase A value | int16 | W | W_SF
40090 | 40090 | 1 | R | 0x03 | WphB | AC Power Phase B value | int16 | W | W_SF
40091 | 40091 | 1 | R | 0x03 | WphC | AC Power Phase C value | int16 | W | W_SF
40092 | 40092 | 1 | R | 0x03 | W_SF |  | sunssf | sunssf
40093 | 40093 | 1 | R | 0x03 | VA | AC Apparent Power value | int16 | VA | VA_SF
40094 | 40094 | 1 | R | 0x03 | VAphA | AC Apparent Power Phase A value | int16 | VA | VA_SF
40095 | 40095 | 1 | R | 0x03 | VAphB | AC Apparent Power Phase B value | int16 | VA | VA_SF
40096 | 40096 | 1 | R | 0x03 | VAphC | AC Apparent Power Phase C value | int16 | VA | VA_SF
40097 | 40097 | 1 | R | 0x03 | VA_SF |  | sunssf | sunssf
40098 | 40098 | 1 | R | 0x03 | VAR | AC Reactive Power value | int16 | VAr | VAR_SF
40099 | 40099 | 1 | R | 0x03 | VARphA | AC Reactive Power Phase A value | int16 | VAr | VAR_SF
40100 | 40100 | 1 | R | 0x03 | VARphB | AC Reactive Power Phase B value | int16 | VAr | VAR_SF
40101 | 40101 | 1 | R | 0x03 | VARphC | AC Reactive Power Phase C value | int16 | VAr | VAR_SF
40102 | 40102 | 1 | R | 0x03 | VAR_SF |  | sunssf | sunssf
40103 | 40103 | 1 | R | 0x03 | PF | Power Factor value | int16 | % | PF_SF
40104 | 40104 | 1 | R | 0x03 | PFphA | Power Factor Phase A value | int16 | % | PF_SF
40105 | 40105 | 1 | R | 0x03 | PFphB | Power Factor Phase B value | int16 | % | PF_SF
40106 | 40106 | 1 | R | 0x03 | PFphC | Power Factor Phase C value | int16 | % | PF_SF
40107 | 40107 | 1 | R | 0x03 | PF_SF |  | sunssf | sunssf
40108 | 40109 | 2 | R | 0x03 | TotWhExp | Total Watt-hours Exported | acc32 | Wh | TotWh_SF
40110 | 40111 | 2 | R | 0x03 | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh | TotWh_SF
40112 | 40113 | 2 | R | 0x03 | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh | TotWh_SF
40114 | 40115 | 2 | R | 0x03 | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh | TotWh_SF
40116 | 40117 | 2 | R | 0x03 | TotWhImp | Total Watt-hours Imported | acc32 | Wh | TotWh_SF
40118 | 40119 | 2 | R | 0x03 | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh | TotWh_SF
40120 | 40121 | 2 | R | 0x03 | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh | TotWh_SF
40122 | 40123 | 2 | R | 0x03 | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh | TotWh_SF
40124 | 40124 | 1 | R | 0x03 | TotWh_SF |  | sunssf | sunssf
40125 | 40126 | 2 | R | 0x03 | TotVAhExp | Total VA-hours Exported | acc32 | VAh | TotVAh_SF
40127 | 40128 | 2 | R | 0x03 | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh | TotVAh_SF
40129 | 40130 | 2 | R | 0x03 | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh | TotVAh_SF
40131 | 40132 | 2 | R | 0x03 | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh | TotVAh_SF
40133 | 40134 | 2 | R | 0x03 | TotVAhImp | Total VA-hours Imported | acc32 | VAh | TotVAh_SF
40135 | 40136 | 2 | R | 0x03 | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh | TotVAh_SF
40137 | 40138 | 2 | R | 0x03 | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh | TotVAh_SF
40139 | 40140 | 2 | R | 0x03 | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh | TotVAh_SF
40141 | 40141 | 1 | R | 0x03 | TotVAh_SF |  | sunssf | sunssf
40142 | 40143 | 2 | R | 0x03 | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | VArh | TotVArh_SF | register not supported
40144 | 40145 | 2 | R | 0x03 | TotVArhImpQ1phA | Total VAR-hours Imported Q1 phase A | acc32 | VArh | TotVArh_SF | register not supported
40146 | 40147 | 2 | R | 0x03 | TotVArhImpQ1phB | Total VAR-hours Imported Q1 phase B | acc32 | VArh | TotVArh_SF | register not supported
40148 | 40149 | 2 | R | 0x03 | TotVArhImpQ1phC | Total VAR-hours Imported Q1 phase C | acc32 | VArh | TotVArh_SF | register not supported
40150 | 40151 | 2 | R | 0x03 | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | VArh | TotVArh_SF | register not supported
40152 | 40153 | 2 | R | 0x03 | TotVArhImpQ2phA | Total VAR-hours Imported Q2 phase A | acc32 | VArh | TotVArh_SF | register not supported
40154 | 40155 | 2 | R | 0x03 | TotVArhImpQ2phB | Total VAR-hours Imported Q2 phase B | acc32 | VArh | TotVArh_SF | register not supported
40156 | 40157 | 2 | R | 0x03 | TotVArhImpQ2phC | Total VAR-hours Imported Q2 phase C | acc32 | VArh | TotVArh_SF | register not supported
40158 | 40159 | 2 | R | 0x03 | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | VArh | TotVArh_SF | register not supported
40160 | 40161 | 2 | R | 0x03 | TotVArhExpQ3phA | Total VAR-hours Exported Q3 phase A | acc32 | VArh | TotVArh_SF | register not supported
40162 | 40163 | 2 | R | 0x03 | TotVArhExpQ3phB | Total VAR-hours Exported Q3 phase B | acc32 | VArh | TotVArh_SF | register not supported
40164 | 40165 | 2 | R | 0x03 | TotVArhExpQ3phC | Total VAR-hours Exported Q3 phase C | acc32 | VArh | TotVArh_SF | register not supported
40166 | 40167 | 2 | R | 0x03 | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | VArh | TotVArh_SF | register not supported
40168 | 40169 | 2 | R | 0x03 | TotVArhExpQ4phA | Total VAR-hours Exported Q4 phase A | acc32 | VArh | TotVArh_SF | register not supported
40170 | 40171 | 2 | R | 0x03 | TotVArhExpQ4phB | Total VAR-hours Exported Q4 phase B | acc32 | VArh | TotVArh_SF | register not supported
40172 | 40173 | 2 | R | 0x03 | TotVArhExpQ4phC | Total VAR-hours Exported Q4 phase C | acc32 | VArh | TotVArh_SF | register not supported
40174 | 40174 | 1 | R | 0x03 | TotVArh_SF |  | sunssf | sunssf |  | register not supported
40175 | 40176 | 2 | R | 0x03 | Evt | Events | bitfield32
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40177 | 40177 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
40178 | 40178 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0

## C001 Common
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 2 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
3 | 3 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
4 | 4 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
5 | 20 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
21 | 36 | 16 | R | 0x03 | Md | Device model | String32
37 | 44 | 8 | R | 0x03 | Opt | Options | String16
45 | 52 | 8 | R | 0x03 | Vr | SW version of meter | String16
53 | 68 | 16 | R | 0x03 | SN | Serialnumber of the meter | String32
69 | 69 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1-247

## M20X Meter
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Meter Modbus Map; 201: single phase, 202: split phase, 203: three phase | uint16 |  |  | 201, 202, 203
2 | 2 | 1 | R | 0x03 | L | Length of inverter model block | uint16 | Registers |  | 105
3 | 3 | 1 | R | 0x03 | A | AC Total Current value | int16 | A | A_SF
4 | 4 | 1 | R | 0x03 | AphA | AC Phase-A Current value | int16 | A | A_SF
5 | 5 | 1 | R | 0x03 | AphB | AC Phase-B Current value | int16 | A | A_SF
6 | 6 | 1 | R | 0x03 | AphC | AC Phase-C Current value | int16 | A | A_SF
7 | 7 | 1 | R | 0x03 | A_SF |  | int16 | sunssf
8 | 8 | 1 | R | 0x03 | PhV | AC Voltage Average Phase-to-neutral value | int16 | V | V_SF
9 | 9 | 1 | R | 0x03 | PhVphA | AC Voltage Phase-A-to-neutral value | int16 | V | V_SF
10 | 10 | 1 | R | 0x03 | PhVphB | AC Voltage Phase-B-to-neutral value | int16 | V | V_SF
11 | 11 | 1 | R | 0x03 | PhVphC | AC Voltage Phase-C-to-neutral value | int16 | V | V_SF
12 | 12 | 1 | R | 0x03 | PPV | AC Voltage Average Phase-to-phase value | int16 | V | V_SF
13 | 13 | 1 | R | 0x03 | PPVphAB | AC Voltage Phase-AB value | int16 | V | V_SF
14 | 14 | 1 | R | 0x03 | PPVphBC | AC Voltage Phase-BC value | int16 | V | V_SF
15 | 15 | 1 | R | 0x03 | PPVphCA | AC Voltage Phase-CA value | int16 | V | V_SF
16 | 16 | 1 | R | 0x03 | V_SF |  | int16 | sunssf
17 | 17 | 1 | R | 0x03 | Hz | AC Frequency value | int16 | Hz | Hz_SF
18 | 18 | 1 | R | 0x03 | Hz_SF |  | int16 | sunssf
19 | 19 | 1 | R | 0x03 | W | AC Power value | int16 | W | W_SF
20 | 20 | 1 | R | 0x03 | WphA | AC Power Phase A value | int16 | W | W_SF
21 | 21 | 1 | R | 0x03 | WphB | AC Power Phase B value | int16 | W | W_SF
22 | 22 | 1 | R | 0x03 | WphC | AC Power Phase C value | int16 | W | W_SF
23 | 23 | 1 | R | 0x03 | W_SF |  | int16 | sunssf
24 | 24 | 1 | R | 0x03 | VA | AC Apparent Power value | int16 | VA | VA_SF
25 | 25 | 1 | R | 0x03 | VAphA | AC Apparent Power Phase A value | int16 | VA | VA_SF
26 | 26 | 1 | R | 0x03 | VAphB | AC Apparent Power Phase B value | int16 | VA | VA_SF
27 | 27 | 1 | R | 0x03 | VAphC | AC Apparent Power Phase C value | int16 | VA | VA_SF
28 | 28 | 1 | R | 0x03 | VA_SF |  | int16 | sunssf
29 | 29 | 1 | R | 0x03 | VAR | AC Reactive Power value | int16 | VAr | VAR_SF
30 | 30 | 1 | R | 0x03 | VARphA | AC Reactive Power Phase A value | int16 | VAr | VAR_SF
31 | 31 | 1 | R | 0x03 | VARphB | AC Reactive Power Phase B value | int16 | VAr | VAR_SF
32 | 32 | 1 | R | 0x03 | VARphC | AC Reactive Power Phase C value | int16 | VAr | VAR_SF
33 | 33 | 1 | R | 0x03 | VAR_SF |  | int16 | sunssf
34 | 34 | 1 | R | 0x03 | PF | Power Factor value | int16 | % | PF_SF
35 | 35 | 1 | R | 0x03 | PFphA | Power Factor Phase A value | int16 | % | PF_SF
36 | 36 | 1 | R | 0x03 | PFphB | Power Factor Phase B value | int16 | % | PF_SF
37 | 37 | 1 | R | 0x03 | PFphC | Power Factor Phase C value | int16 | % | PF_SF
38 | 38 | 1 | R | 0x03 | PF_SF |  | int16 | sunssf
39 | 40 | 2 | R | 0x03 | TotWhExp | Total Watt-hours Exported | uint32 | Wh | TotWh_SF
41 | 42 | 2 | R | 0x03 | TotWhExpPhA | Total Watt-hours Exported phase A | uint32 | Wh | TotWh_SF
43 | 44 | 2 | R | 0x03 | TotWhExpPhB | Total Watt-hours Exported phase B | uint32 | Wh | TotWh_SF
45 | 46 | 2 | R | 0x03 | TotWhExpPhC | Total Watt-hours Exported phase C | uint32 | Wh | TotWh_SF
47 | 48 | 2 | R | 0x03 | TotWhImp | Total Watt-hours Imported | uint32 | Wh | TotWh_SF
49 | 50 | 2 | R | 0x03 | TotWhImpPhA | Total Watt-hours Imported phase A | uint32 | Wh | TotWh_SF
51 | 52 | 2 | R | 0x03 | TotWhImpPhB | Total Watt-hours Imported phase B | uint32 | Wh | TotWh_SF
53 | 54 | 2 | R | 0x03 | TotWhImpPhC | Total Watt-hours Imported phase C | uint32 | Wh | TotWh_SF
55 | 55 | 1 | R | 0x03 | TotWh_SF |  | int16 | sunssf
56 | 57 | 2 | R | 0x03 | TotVAhExp | Total VA-hours Exported | uint32 | VAh | TotVAh_SF
58 | 59 | 2 | R | 0x03 | TotVAhExpPhA | Total VA-hours Exported phase A | uint32 | VAh | TotVAh_SF
60 | 61 | 2 | R | 0x03 | TotVAhExpPhB | Total VA-hours Exported phase B | uint32 | VAh | TotVAh_SF
62 | 63 | 2 | R | 0x03 | TotVAhExpPhC | Total VA-hours Exported phase C | uint32 | VAh | TotVAh_SF
64 | 65 | 2 | R | 0x03 | TotVAhImp | Total VA-hours Imported | uint32 | VAh | TotVAh_SF
66 | 67 | 2 | R | 0x03 | TotVAhImpPhA | Total VA-hours Imported phase A | uint32 | VAh | TotVAh_SF
68 | 69 | 2 | R | 0x03 | TotVAhImpPhB | Total VA-hours Imported phase B | uint32 | VAh | TotVAh_SF
70 | 71 | 2 | R | 0x03 | TotVAhImpPhC | Total VA-hours Imported phase C | uint32 | VAh | TotVAh_SF
72 | 72 | 1 | R | 0x03 | TotVAh_SF |  | int16 | sunssf
73 | 74 | 2 | R | 0x03 | TotVArhImpQ1 | Total VAR-hours Imported Q1 | uint32 | VArh | TotVArh_SF | register not supported
75 | 76 | 2 | R | 0x03 | TotVArhImpQ1phA | Total VAR-hours Imported Q1 phase A | uint32 | VArh | TotVArh_SF | register not supported
77 | 78 | 2 | R | 0x03 | TotVArhImpQ1phB | Total VAR-hours Imported Q1 phase B | uint32 | VArh | TotVArh_SF | register not supported
79 | 80 | 2 | R | 0x03 | TotVArhImpQ1phC | Total VAR-hours Imported Q1 phase C | uint32 | VArh | TotVArh_SF | register not supported
81 | 82 | 2 | R | 0x03 | TotVArhImpQ2 | Total VAr-hours Imported Q2 | uint32 | VArh | TotVArh_SF | register not supported
83 | 84 | 2 | R | 0x03 | TotVArhImpQ2phA | Total VAR-hours Imported Q2 phase A | uint32 | VArh | TotVArh_SF | register not supported
85 | 86 | 2 | R | 0x03 | TotVArhImpQ2phB | Total VAR-hours Imported Q2 phase B | uint32 | VArh | TotVArh_SF | register not supported
87 | 88 | 2 | R | 0x03 | TotVArhImpQ2phC | Total VAR-hours Imported Q2 phase C | uint32 | VArh | TotVArh_SF | register not supported
89 | 90 | 2 | R | 0x03 | TotVArhExpQ3 | Total VAr-hours Exported Q3 | uint32 | VArh | TotVArh_SF | register not supported
91 | 92 | 2 | R | 0x03 | TotVArhExpQ3phA | Total VAR-hours Exported Q3 phase A | uint32 | VArh | TotVArh_SF | register not supported
93 | 94 | 2 | R | 0x03 | TotVArhExpQ3phB | Total VAR-hours Exported Q3 phase B | uint32 | VArh | TotVArh_SF | register not supported
95 | 96 | 2 | R | 0x03 | TotVArhExpQ3phC | Total VAR-hours Exported Q3 phase C | uint32 | VArh | TotVArh_SF | register not supported
97 | 98 | 2 | R | 0x03 | TotVArhExpQ4 | Total VAr-hours Exported Q4 | uint32 | VArh | TotVArh_SF | register not supported
99 | 100 | 2 | R | 0x03 | TotVArhExpQ4phA | Total VAR-hours Exported Q4 phase A | uint32 | VArh | TotVArh_SF | register not supported
101 | 102 | 2 | R | 0x03 | TotVArhExpQ4phB | Total VAR-hours Exported Q4 phase B | uint32 | VArh | TotVArh_SF | register not supported
103 | 104 | 2 | R | 0x03 | TotVArhExpQ4phC | Total VAR-hours Exported Q4 phase C | uint32 | VArh | TotVArh_SF | register not supported
105 | 105 | 1 | R | 0x03 | TotVArh_SF |  | int16 | sunssf |  | register not supported
106 | 107 | 2 | R | 0x03 | Evt | Events | uint32

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0